## GP Analysis of LEED BD+C
LEED BD+C |  |  | System Owner Survey Response
GBCS review criteria | Guiding Principle | GP Compliance Language | Does System address Criteria? | What credit/criteria numbers did the system owner reference? | Which criteria are mandatory/ optional? | Is answer complete? | Validate Answer: do credit(s)/criteria address GP? | What Part of the GP criteria does the system credit/criteria meet? | Does credit/criteria partially or fully meet criteria? | How should this be scored? (Green = Fully aligns with and meets GP criteria; Yellow = partially aligns with and meets GP criteria; Red = system does not address criteria) | Notes | Meet GP? | Prerequisite / Credits needed to meet GP | Points
Part II - Employ Integrated Design Principles
Integrated design and management | GP NC&M 1.1 Integrated Design and Management | Page 16 | Yes | LEED v4.1 BD+C includes a mandatory prerequisite for Integrative Project Planning & Design that applies only to Healthcare projects, and an optional credit for Integrative Process that applies to all projects. LEED v4.1 Prerequisite: Integrative Project Planning & Design (page 8) is for Healthcare projects, and is unchanged from LEED v4. It requires the team to: Use cross-discipline design and decision making, beginning in the programming and pre-design phase. At a minimum, prepare an Owner’s Project Requirements (OPR) document incorporating a health mission statement; develop preliminary rating goals; assemble an integrated project team; and conduct a design charrette. LEED v4.1 Credit: Integrative Process (page 9) is for all projects and has minor changes from LEED v4. The credit requirements are: "Beginning in pre-design and continuing throughout the design phases, identify and use opportunities to achieve synergies across disciplines and building systems." Project teams must conduct a suite of analyses in at least two of the following: energy systems, water systems, site selection, social equity, and health & wellbeing. Implementation requires having an Integrative Process Facilitator and developing an agreed-to and signed project team letter with a clearly defined process and goals for each area. In addition, the Sustainable Sites credit: Tenant Design and Construction Guidelines (page 47) supports integrated design across the owner and tenant. | Mandatory/Optional | Yes | Yes | GP NC&M 1.1 Integrated Design and Management | Fully | Green |  |  | Credit: Integrative Process
Access to public amenities/neighborhood assets | GP NC&M 1.2 Sustainable Siting | Page 16 | Yes | The LEED v4.1 Location & Transportation credit: Surrounding Density and Diverse Uses (page 16) addresses access to public amenities and neighborhood assets. This optional credit has minor changes from LEED v4. | Optional | Yes | Yes | GP NC&M 1.2 Sustainable Siting - Option 1 - Location & Transporation credit: Surrounding Density and Diverse Uses: To conserve land and protect farmland and wildlife habitat by encouraging development in areas with existing infrastructure. To support neighborhood and local economies promote walkability and low or no carbon transportation, and reduce vehicle distance traveled for all. To improve public health by encouraging daily physical activity. | Fully | Green |  |  | Credit: Location & Transportation - Surrounding Density and Diverse Uses
Floodplain avoidance | GP NC&M 1.2 Sustainable Siting | Page 16 | Yes | Two LEED v4.1 BD+C credits addresses floodplain avoidance by considering project location relative to environmentally sensitive lands. LEED v4.1 Sustainable Sites credit: Site Assessment (page 34) requires project teams to complete and document a site survey or assessment that includes information on hydrology such as consideration of flood hazards areas, among other factors. This optional credit has minor changes from LEED v4. Specifically, the intent now includes environmental justice concerns and cultural and social factors among the listed site conditions to be evaluat | Optional | Yes | Yes | GP NC&M 1.2 Sustainable Siting - Option 1 - Sustainable Sites credit: Site Assessment (page 34) requires project teams to complete and document a site survey or assessment that includes information on hydrology such as consideration of flood hazards areas, among other factors. | Fully | Green |  |  | Credit: Sustainable Sites - Site Assessment Credit: Location & Transportation - Sensitive Land Protection
Protection of historic resources | GP NC&M 1.2 Sustainable Siting | Page 16 | Yes | LEED v4.1 Materials & Resources credit: Building Life-Cycle Impact Reduction (page 94) addresses protection of historic resources by rewarding projects reusing buildings, including historic buildings. Option 1 of this credit addresses historic building reuse. Achievement requires projects to maintain the existing building structure, envelope, and /or interior elements of a historic building, except elements that are structurally unsound or hazardous. This optional credit has major changes from LEED v4. In addition, LEED v4.1 Environmental Quality prerequisite: Minimum Indoor Air Quality Performance has a specific pathway (option 3, page 114) available to historic structures to help facilitate preservation (option 3, page 114), and the prerequisite: Minimum Acoustic Performance has an exception for the same reason (page 117). | Optional | Yes | Yes | GP NC&M 1.2 Sustainable Siting - Option 1 - Materials & Resources credit: Building Life-Cycle Impact Reduction uses historic properties and addresses protection of historic resources by rewarding projects reusing buildings, including historic buildings. | Fully | Green |  |  | Credit: Materials & Resources - Building Life-Cycle Impact Reduction
Preservation and protection of surrounding areas and habitats | GP NC&M 1.2 Sustainable Siting | Page 16 | Yes | LEED v4.1 BD+C has four credits directly addressing the preservation and protection of surrounding areas and habitats, and a number of others contributing to this outcome. LEED v4.1 Location & Transportation credit: Sensitive Land Protection (page 13) requires location on previously developed land, or avoiding sensitive areas which include certain habitat classifications. This optional credit has minor changes from LEED v4. LEED v4.1 Sustainable Sites credit: Protect or Restore Habitat (page 36) requires preserving and protecting a portion of the greenfield area on the site and restoring a portion of the site identified as previously disturbed, with requirements for soil and vegetation. This optional credit has minor changes from LEED v4. LEED v4.1 Sustainable Sites credit: Open Space (page 38) requires providing a certain amount of open space some of which must be a listed type of green space whereby habitat is one of the options; and having two types of vegetation or vegetated canopy. This optional credit has minor changes from LEED v4. LEED v4.1 Sustainable Sites credit: Heat Island Reduction (page 40) minimizes negative heat effects on microclimates and human and wildlife habitats. This optional credit has minor changes from LEED v4. Several other LEED v4.1 BD+C prerequisites and credits may contribute to protecting surrounding land and habitat, such as the Sustainable Sites mandatory prerequisite: Construction Activity Pollution Prevention (page 32) and he Sustainable Sites optional credit: Rainwater Management (page 39) as both could help prevent excess or contaminated stormwater from running offsite and adversely impacting other land. Also, the Sustainable Sites prerequisite (for health care and schools): Environmental Site Assessment (page 33) and the Sustainable Sites credit: Site Assessment (page 34), could lead to protecting surrounding land through identifying sensitive and special areas and features as well as contamination. Additionally, some pilot credits have benefits to habitat. For example, the Bird Collision Deterrence pilot credit (SSpc55) effectively makes bird habitat around a building safer. | Mandatory/Optional | Yes | Yes | GP NC&M 1.2 Sustainable Siting - Option 1 - Location & Transportation credit: Sensitive Land Protection requires location on previously developed land, or avoiding sensitive areas which include certain habitat classifications. Sustainable Sites credit: Protect or Restore Habitat requires preserving and protecting a portion of the greenfield area on the site and restoring a portion of the site identified as previously disturbed, with requirements for soil and vegetation. Sustainable Sites credit: Open Space requires providing a certain amount of open space some of which must be a listed type of green space whereby habitat is one of the options; and having two types of vegetation or vegetated canopy. Sustainable Sites credit: Heat Island Reduction minimizes negative heat effects on microclimates and human and wildlife habitats. | Fully | Green |  |  | Prerequisite: Sustainable Sites - Construction Activity Pollution Prevention Credit: Location & Transportation - Sensitive Land Protection Credit: Sustainable Sites - Protect or Restore Habitat Credit: Sustainable Sites - Open Space
Stormwater management | GP NC&M 1.3 Stormwater Management | Page 17 | Yes | LEED v4.1 BD+C Sustainable Sites mandatory prerequisite: Construction Activity Pollution Prevention (page 32) addresses stormwater during construction. Sustainable Sites credit: Rainwater Management (page 39) addresses post-construction stormwater management by focusing on a more holistic site water management that relies on green infrastructure and low-impact development strategies to replicate the natural hydrology and water balance of the site (and thus improve quality). This optional credit has major changes from LEED v4. Additional credits that help address stormwater management include the LEED v4.1 Location + Transportation credit: Reduced Parking Footprint (page 28) and Sustainable Sites credit: Site Assessment (page 34) which could help avoid contamination and excess runoff. Also, Sustainable Sites credit: Open Space (page 38) and Sustainable Sites credit: Heat Island Reduction (page 40) could benefit stormwater by encouraging green space, vegetation, and shade . These are all optional credits. | Mandatory/Optional | Yes | Yes | GP NC&M 1.3 Stormwater Management - Option 1 met - Sustainable Sites credit: Rainwater Management requires projects to replicate natural site hydrology processes, retain on site the runoff from the associated percentile of regional or local rainfall events using low-impact development (LID) and green infrastructure (GI) practices. However, no mention of surface area coverage. | Fully | Green |  |  | Prerequisite: Sustainable Sites - Construction Activity Pollution Prevention Credit: Sustainable Sites - Rainwater Management
Access to public transportation | GP NC&M 1.4 Infrastructure Utilization and Optimization | Page 17 | Yes | LEED v4.1 BD+C Location + Transportation credit: Access to Quality Transit (page 21) addresses reduced impacts from transportation through building location and site design to promote access to public transit. This credit requires teams to locate the project within 1/4 mile of bus, streetcar or rideshare stops, or within a 1/2 mile of bus rapid transit, rail or commuter ferry terminals; or to provide project-sponsored transit service; and includes specific service thresholds. This is an optional credit. | Optional | Yes | Yes | GP NC&M 1.4 Infrastructure Utilization and Optimization - Option 1 - Location + Transportation credit: This credit requires teams to locate any functional entry of the project within a ¼-mile (400-meter) walking distance of existing or planned bus, streetcar, or informal transit stops, or within a ½-mile (800-meter) walking distance of existing or planned bus rapid transit stops, passenger rail stations (i.e. light, heavy, or commuter rail) or commuter ferry terminals. | Fully | Green |  |  | Credit: Location & Transportation - Access to Quality Transit
Consideration of occupant transportation emissions | GP NC&M 1.4 Infrastructure Utilization and Optimization | Page 17 | Yes | LEED v4.1 BD+C credits address consideration of occupant transportation emissions by rewarding provision of EV infrastructure and biking facilities, as well as thoughtful decisions about building location that encourage compact development, alternative transportation and walkability. LEED v4.1 Location + Transportation credit: Electric Vehicles (page 30) requires projects to provide charging infrastructure for electric vehicles for on-site parking. Projects must provide either installed electrical vehicle supply equipment (EVSE) in a certain proportion or number of spaces; or EV Ready, with a dedicated electrical circuit with sufficient capacity for each required space, for double the spaces. This optional credit has major changes from its LEED v4 analog, “Green Vehicles.” LEED v4.1 Location + Transportation credit: Biking Facilities (page 25) promotes zero and low carbon transportation and reduce vehicle distance traveled through bicycling. This optional credit has minor changes from LEED v4. LEED v4.1 Location + Transportation credit: Reduced Parking Footprint (page 28) also helps reduce vehicle emissions associated with the building through reducing off-site parking spaces. This optional credit has major changes from LEED v4. LEED v4.1 Location + Transportation credit: Surrounding Density and Diverse Uses (page 16) promotes walkability and transport efficiency, thereby helping reduce occupant transportation emissions, by encouraging nearby density and availability of public amenities and neighborhood assets. This optional credit has minor changes from LEED v4. | Optional | Yes | Yes | GP NC&M 1.4 Infrastructure Utilization and Optimization - Option 1 met - Location + Transportation credit: This credit requires teams to locate any functional entry of the project within a ¼-mile (400-meter) walking distance of existing or planned bus, streetcar, or informal transit stops, or within a ½-mile (800-meter) walking distance of existing or planned bus rapid transit stops, passenger rail stations. Option 2 met - Location + Transportation credit: Electric Vehicles requires the installation of EV supply equipment (EVSE) in 5% of all parking spaces used by the project or at least two spaces, whichever is greater. Option 4 met - Location + Transportation credit: Biking Facilities promotes bicycling and transportation efficiency and reduce vehicle distance traveled by requiring projects to be located within 200 yards of a bicycle from bicycle storage. Location + Transportation credit: Surrounding Density and Diverse Uses promotes walkability and transport efficiency to reduce occupant transportation emissions, by encouraging nearby density and availability of public amenities and neighborhood assets. | Fully | Green |  |  | Credit: Location + Transportation - Electric Vehicles Credit: Location + Transportation - Biking Facilities Credit: Location + Transportation - Reduced Parking Footprint Credit: Location + Transportation - Surrounding Density and Diverse Uses
Commissioning | GP NC&M 1.5 Commissioning | Page 18 | Yes | LEED v4.1 BD+C includes a mandatory prerequisite for commissioning and an optional credit for enhanced commissioning. LEED v4.1 Energy + Atmosphere prerequisite: Fundamental Commissioning and Verification (page 67) requires the commissioning of mechanical, electrical, plumbing, and renewable energy systems and assemblies, in accordance with ASHRAE Guideline 0-2005 and ASHRAE Guideline 1.1-2007 by a qualified commissioning authority. There are also some commissioning requirements for exterior enclosures. The prerequisite also requires that an operations and maintenance plan be developed for ongoing operations. This mandatory prerequisite had minor changes from LEED v4. LEED v4.1 Energy + Atmosphere credit: Enhanced Commissioning (page 73) provides points for various levels of additional commissioning activities beyond those required in the prerequisite. For example, one option provides for an expanded set of review and verification functions by the commissioning authority, including a review of building operations 10 months after substantial completion; another option uses monitoring-based commissioning. An additional option is to complete commissioning process (CxP) activities for the building’s thermal envelope in accordance with ASHRAE Guideline 0–2013 and ASTM E2947-16: Standard Guide for Building Enclosure Commissioning, including additional verification steps and a review of building operations 10 months after substantial completion. This voluntary credit had minor changes from LEED v4. Additionally, under the LEED v4.1 Energy + Atmosphere credit: Grid Harmonization (page 84) requires the demand response and/or grid resilience technology be included in the commissioning scope of work. This voluntary credit had minor changes from LEED v4. Commissioning outcomes are referenced in several other credits as well. | Mandatory/Optional | Yes | Yes | GP NC&M 1.5 Commissioning - Option 1 met - LEED v4.1 Energy + Atmosphere prerequisite: Fundamental Commissioning and Verification requires the commissioning of mechanical, electrical, plumbing, and renewable energy systems and assemblies, in accordance with ASHRAE Guideline 0-2005 and ASHRAE Guideline 1.1-2007 by a qualified commissioning authority. | Fully | Green |  |  | Prerequisite: Energy & Atmosphere - Fundamental Commissioning and Verification Credit: Energy & Atmosphere - Enhanced Commissioning
Part II - Optimize Energy Performance
Energy use reduction | GP NC&M 2.1 Energy Efficiency | Page 19 | Yes | LEED v4.1 BD+C addresses actual energy use reduction primarily through a mandatory prerequisite for minimum energy performance and an optional credit for optimized energy performance. Additional credits in various categories also contribute to reduce the building project’s overall energy use; for example, requirements for water efficiency also help save energy. And, the commissioning and verification process helps optimize system performance and reduce long term maintenance issues and wasted energy by verifying that the design meets the owner’s project requirements and functions as intended. LEED v4.1 Energy + Atmosphere prerequisite: Minimum Energy Performance (page 69) requires projects to achieve a minimum level of energy efficiency for the whole building and its systems. This mandatory prerequisite had major changes from LEED v4. For example, this prerequisite references ASHRAE 90.1-2016, projects must implement all mandatory provisions and comply with one of three options – prescriptive requirements; whole building energy cost budget method; or whole building performance rating method. LEED v4.1 Energy + Atmosphere credit: Optimize Energy Performance (page 76) awards points to projects that achieve further levels of energy efficiency for the whole building and its systems. This voluntary credit had major changes from LEED v4. For example, the credit references ASHRAE 90.1-2016 as the baseline. There are three main pathways, all of which address deep energy efficiency. Under Option 1, points are calculated based on the whole building percent improvement (performance cost index) below the target, using two metrics: cost and GHG emissions. Alternately, under Option 2, projects may comply with the appropriate 50% Advanced Energy Design Guide, in addition to meeting the ASHRAE 90.1-2016 prescriptive compliance path. Lastly, Option 3 awards points for achieving specific systems-based energy efficiency levels. | Mandatory/Optional | Yes | Yes | GP NC&M 2.1 Energy Efficiency | Partially | Yellow | To meet the Guiding Principles, agencies would need to ensure that their projects be 30% more efficient than ASHRAE 90.1-2013, demonstrate energy use is 20% below FY2015 baseline, demonstrate energy use is 30% below FY2003 baseline, or achieve an Energy Star rating of 75 or higher.
procurement of ENERGY STAR products and/ Federal Energy Management Program or products | GP NC&M 2.1 Energy Efficiency | Page 19 | Yes | LEED v4.1 BD+C addresses ENERGY STAR products in part. (Only “yes” or “no” was an option above) Generally, in order for new construction and major renovations to meet LEED v4.1 Minimum Energy Performance and to achieve critical points in the Optimize Energy Performance credit, using ENERGY STAR appliances is likely. There are specific references to ENERGY STAR in several credits. (1) In LEED v4.1 Water Efficiency prerequisite: Indoor Water Use Reduction (page 53), certain appliances must be ENERGY STAR or the performance equivalent (page 54). This mandatory prerequisite has minor changes from LEED v4. (2) In LEED v4.1 Energy + Atmosphere credit: Optimize Energy Performance, the systems optimization option provides for ENERGY STAR equipment and appliances (page 80). This voluntary credit has major changes from LEED v4. (3) In LEED v4.1 Materials + Resources prerequisite (healthcare only) and its companion voluntary credit for PBT Source Reduction for Mercury, certain lights must be ENERGY STAR (page 93, page 104). (4) Additionally, in the Location + Transportation credit: Electric Vehicles, if EVSE is used, it must meet the connected functionality criteria for ENERGY STAR certified EVSE (page 30). | Mandatory/Optional | Yes | Yes | GP NC&M 2.1 Energy Efficiency | Partially | Yellow | To meet the Guiding Principles, agencies should purchase Energy Star or FEMP-designated products where possible. While there are credits agencies can choose from below, these will not achieve total compliance with the Guiding Principles. The rating system references Energy Star for water-use products , but it does not reference Energy Star for other products nor does it require that Energy Star products be purchased. |  | Option 3 of Energy and Atmosphere credit Optimize Energy Performance
Energy metering | GP NC&M 2.2 Energy Metering | Page 19 | Yes | LEED v4.1 BD+C requires meters for building level electricity, natural gas, and steam meters as well as tracking data, through a mandatory requisite, and also rewards advanced metering with an optional credit. LEED v4.1 Energy + Atmosphere prerequisite: Building-Level Energy Metering (page 71) requires that building-level energy meters are installed (electricity, natural gas, chilled water, steam, fuel oil, propane, biomass, etc.); projects may use sub-meters that have the ability to aggregate data for whole building reporting. Projects are required to commit to five years of reporting energy data to USGBC for data aggregation and analysis, unless a special exception is provided for security reasons (as has been provided for the Department of Defense). USGBC also accepts data from approved sources. USGBC works to reduce disparities between predictive and actual performance by analyzing data and sharing results. This mandatory prerequisite is unchanged from LEED v4. LEED v4.1 Energy + Atmosphere prerequisite: Advanced Energy Metering (page 82) provides points to a project that also installs meters to energy end uses that represent 10% or more of the total building energy consumption. The advanced metering must meet specific characteristics including a data collection system that uses a local area network, building automation system, wireless network, or comparable communication infrastructure. This optional credit is unchanged from LEED v4. | Mandatory/Optional | Yes | Yes | GP NC&M 2.2 Energy Metering | Fully | Green |  |  | Prerequisite: Energy + Atmosphere - Building-Level Energy Metering Prerequisite: Energy + Atmosphere - Advanced Energy Metering
Renewable energy | GP NC&M 2.3 Renewable Energy | Page 20 | Yes | LEED v4.1 BD+C addresses renewable energy directly through an optional credit with points to projects that produce renewable energy on-site and certain off-site renewable energy systems meeting conditions such as retention of environmental attribute credits (also referred to as RECs). The LEED v4.1 Energy + Atmosphere prerequisite and credit on commissioning also address renewable energy systems by including them in scope to support well-functioning RE systems. Other LEED v4.1 credits indirectly reward renewable energy, notably the Energy + Atmosphere credit: Optimize Energy Performance , which includes a GHG metric in conjunction with an energy efficiency metric; and some of the Materials + Resources credits involve reducing product lifecycle impact, which can encourage renewable energy through the supply chain. LEED v4.1 Energy + Atmosphere credit: Renewable Energy (page 86) awards points to projects that include new on-site renewable energy generation and/or qualified off-site renewable energy; points are awarded based on the portion of total site energy use provided, from 2 to 100 percent, and according to tiers whereby new on-site generation is most heavily rewarded. All environmental attributes (RECs) must be retained and retired. Off-site renewable energy must be Green-E certified. This optional credit has major changes from LEED v4. Notably, the new v4.1 credit combines two LEED v4 credits, Renewable Energy Production and Green Power and Carbon Offsets, into a single 5-point credit that recognizes on-site and off-site renewable energy procurement. | Optional | Yes | Yes | GP NC&M 2.3 Renewable Energy | Fully | Green |  |  | Credit: Energy & Atmosphere - Renewable Energy
Benchmarking | GP NC&M 2.4 Benchmarking | Page 20 | Yes | LEED v4.1 BD+C addresses benchmarking first by requiring whole building metering; and second by requires projects to document post-occupancy energy use. LEED v4.1 Energy + Atmosphere prerequisite: Building-Level Energy Metering (page 71) requires the installation of building level meters or sub-meters that have the ability to aggregate data for whole building reporting. This mandatory prerequisite sets the stage for benchmarking and requires the project to commit to share post-occupancy data, on a monthly interval, with USGBC for five years (some exceptions may be authorized for security reasons). Finally, LEED BD+C projects are encouraged to conduct benchmarking and are set up in USGBC’s free performance platform, Arc, should a project team wish to use the system. | Mandatory | Yes | Yes | GP NC&M 2.4 Benchmarking | Partially | Yellow | To meet the Guiding Principles, agencies need to benchmark building performance each year, preferably in Energy Star Portfolio Manager. The rating system encourages metering energy use and monitoring on a monthly basiss as well as sharing the info with USGBC; however, the rating system does not require annual benchmarking.
Part II - Protect and Conserve Water
Indoor water use reduction | GP NC&M 3.1 Indoor Water Use | Page 21 | Yes | LEED v4.1 BD+C addresses indoor water user through a prerequisite and a credit that target indoor water efficiency and reductions in use. Additional credits, including those described later in this section such as the Optimize Process Water use credit, also help reduce total indoor water use. LEED v4.1 Water Efficiency prerequisite: Indoor Water Use Reduction (page 53) targets fixture efficiency and requires projects to report water data to USGBC. The prerequisite includes prescriptive requirements for fixtures and appliances, which also must be WaterSense labeled if the item is eligible. The prerequisite also requires projects meet standards for select process water uses. Example measures include: no once-through cooling water, makeup water meters, conductivity controllers, overflow alarms, and drift eliminators. This mandatory prerequisite has minor changes from LEED v4. LEED v4.1 Water Efficiency credit: Indoor Water Use Reduction (page 59) rewards projects that reduce water use beyond the baseline level of the prerequisite, starting with 25 percent reduction. Alternative water sources can also be used to achieve additional (beyond-prerequisite) water savings in this credit. This optional credit has minor changes from LEED v4. Note that several pilot credits and pilot alternative compliance pathways also support indoor water use reduction. For example, the ACP, Whole Project Water Use Reduction, uses a whole project water budget approach, quantifying water use with whole building water balance modeling; while the Integrated Project Water Reuse Strategy pilot credit incentivizes an integrated design process for building water reuse systems. More information on these two optional pilot credits can be found at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-16 and https://www.usgbc.org/credits/WEpc157-v41. | Mandatory/Optional | Yes | Yes | GP NC&M 3.1 Indoor Water Use | Fully | Green |  |  | Prerequisite: Water Efficiency - Indoor Water Use Reduction Credit: Water Efficiency - Indoor Water Use Reduction
Procurement Water conserving products | GP NC&M 3.1 Indoor Water Use | Page 21 | Yes | LEED v4.1 BD+C addresses water conserving products primarily through the two Water Efficiency mandatory prerequisites for Indoor Water Use Reduction and for Outdoor Water Use Reduction, and the companion optional credits for Indoor Water Use Reduction and for Outdoor Water Use Reduction. The prerequisite and credit for Indoor Water Use Reduction address water conserving products through stipulation of specific standards for water efficient fixtures and appliances as an “efficiency first” approach to water conservation. The prerequisite and credit for Outdoor Water Efficiency address water conserving products if the project has irrigation, in that reductions must first be achieved through plant species selection and irrigation system efficiency as calculated through their use of the WaterSense Water Budget Tool. | Mandatory/Optional | Yes | Yes | GP NC&M 3.1 Indoor Water Use | Fully | Green |  |  | Prerequisite: Water Efficiency - Indoor Water Use Reduction Prerequisite: Water Efficiency - Outdoor Water Use Reduction
Water use in cooling equipment | GP NC&M 3.1 Indoor Water Use | Page 21 | Yes | LEED v4.1 BD+C addresses cooling equipment water use primarily through the Water Efficiency credit: Optimize process water use (page 62). Projects can earn points under this credit through several pathways. One calls for reducing cooling tower and evaporative condenser cycles while also ensuring appropriate water quality. Recycled nonpotable water and use of reclaimed water from another process may be used to reduce the amount of water used for cooling tower makeup and maintenance. A second pathway requires a project to increase cooling efficiency by at least 25 percent as compared to a certain baseline cooling tower type. A third option, which can be additional, is to use at least 20% recycled alternative water for use in processes other than cooling. This optional credit has major changes from its analog in LEED v4, known as Cooling Tower Water Use. | Optional | Yes | Yes | GP NC&M 3.1 Indoor Water Use | Fully | Green |  |  | Credit: Water Efficiency - Optimize process water use
Water metering | GP NC&M 3.2 Water Metering | Page 21 | Yes | LEED v4.1 BD+C addresses water metering with a mandatory perquisite and an optional credit. LEED v4.1 Water Efficiency prerequisite: Building-Level Water Metering (page 56), requires metering of total water for a building and associated grounds. Projects are required to share water data with the USGBC over a 5-year period. LEED v4.1 Water Efficiency credit: Water Metering (page 65) awards points for the installation of permanent water meters for two or more of the following water subsystems as they apply to the project: irrigation, indoor plumbing fixtures and fittings, domestic hot water, boilers with aggregate projected annual water use of 100,000 gallons or more, reclaimed water or other process water. Healthcare projects must install water meters in additional systems. One other LEED v4.1 prerequisites require water meters, for example, the Water Efficiency prerequisite: Indoor Water Use Reduction requires cooling towers and evaporative condensors to be equipped with makeup water meters (page 54). | Mandatory/Optional | Yes | Yes | GP NC&M 3.2 Water Metering | Fully | Green |  |  | Prerequisite: Water Efficiency - Building-Level Water Metering Credit: Water Efficiency - Water Metering
Outdoor water use reduction | GP NC&M 3.3 Outdoor Water Use | Page 22 | Yes | LEED v4.1 BD+C credits address actual outdoor water use reduction primarily with a prerequisite and a credit that encourage incorporating native landscapes that eliminate the need for irrigation, and where irrigation is used, to require efficient systems and encourage further efficiency. Several additional Sustainable Sites optional credits reinforce the use of native vegetation which aligns with reduced outdoor water use. LEED v4.1 Water Efficiency prerequisite: Outdoor Water Use Reduction (page 52): requires projects reduce outdoor water use through either incorporating native landscapes eliminating the need for irrigation completely (beyond a maximum two year establishment period), or reducing the project’s landscape water requirement by at least 30% from the calculated baseline for the site’s peak watering month. Reductions must be achieved through plant species selection and irrigation system efficiency as calculated by the EPA WaterSense Budget Tool. This mandatory prerequisite had no changes from LEED v4. LEED v4.1 Water Efficiency credit: Outdoor Water Use Reduction (page 57) rewards projects that either incorporate native landscapes eliminating the need for irrigation completely (beyond a maximum two year establishment period) or reduce the project’s landscape water requirement by at least 50% from the calculated baseline for the site’s peak watering month. This optional credit had minor changes from LEED v4. Note that several pilot credits and pilot alternative compliance pathways also support indoor water use reduction. For example, the ACP, Whole Project Water Use Reduction, features a whole project water budget approach. | Mandatory/Optional | Yes | Yes | GP NC&M 3.3 Outdoor Water Use | Fully | Green |  |  | Prerequisite: Water Efficiency - Outdoor Water Use Reduction Credit: Water Efficiency - Outdoor Water use Reduction
Water efficient landscapes | GP NC&M 3.3 Outdoor Water Use | Page 22 | Yes | LEED v4.1 addresses water efficient landscapes primarily through the Water Efficiency prerequisite and credit for Outdoor Water Use Reduction (page 52, page 57), as described above. Other LEED v4.1 credits reward restoration of local and native plants that can survive on local rainfall, for example Sustainable Sites optional credits: Protect or Restore Habitat (page 36) and Open Space (page 38). LEED v4.1 Water Efficiency prerequisite: Outdoor Water Use Reduction (page 52) and credit: Outdoor Water Use Reduction (page 57) require and reward, accordingly, projects that either incorporate native landscapes eliminating the need for irrigation completely (beyond a maximum two year establishment period) or reduce the project’s landscape water requirement by at least 30% (prerequisite) or 50% (credit) from the calculated baseline for the site’s peak watering month. Additionally, some pilot credits further address water efficient landscape, such as one rewarding the use of landscaping for native food production. | Optional | Yes | Yes | GP NC&M 3.3 Outdoor Water Use | Fully | Green |  |  | Prerequisite: Water Efficiency - Outdoor Water Use Reduction Credit: Water Efficiency - Outdoor Water use Reduction
Alternative sources of water | GP NC&M 3.4 Alternative Water | Page 22 | Yes | LEED v4.1 BD+C address alternative sources of water in several prerequisites and credits. After first reducing water consumption through fixture, fittings, and process water practices, projects can be rewarded for additional potable water savings using alternative water sources. LEED v4.1 Water Efficiency credit: Indoor Water Use Reduction (page 59) rewards projects for achieving at least 25% reduction over baseline. Additional potable water savings beyond the prerequisite level can be earned using alternative water sources. This voluntary credit has minor changes from LEED v4. LEED v4.1 Water Efficiency credit: Outdoor Water Use Reduction (page 57), as described above, rewards projects for reducing their outdoor water use by 50%, whereby savings beyond 30% can be achieved by a combination of efficiency, alternative water sources and smart scheduling technologies. This voluntary credit has minor changes from LEED v4. Pilot credits also encourage alternative sources of water. For example, the Integrated Water Reuse Strategy (view at https://www.usgbc.org/credits/WEpc157-v41 )and the Water Restoration Certificates (view at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-33) each encourage alternative water sources. | Optional | Yes | Yes | GP NC&M 3.4 Alternative Water | Fully | Green |  |  | Credit: Water Efficiency - Indoor Water Use Reduction Credit: Water Efficiency - Outdoor Water Use Reduction
Part II - Enhance the Indoor Environment
Ventilation and thermal comfort | GP NC&M 4.1 Ventilation and Thermal Comfort | Page 23 | Yes | Four LEED v4.1 BD+C prerequisites/credits address ventilation and thermal control. LEED v4.1 addresses ventilation with a prerequisite and a credit for indoor air quality. The Environmental Quality prerequisite: Minimum Indoor Air Quality Performance (page 113) requires meeting requirements for both ventilation and monitoring. This mandatory prerequisite has major changes from LEED v4. LEED v4.1 BD+C Environmental Quality credit: Enhanced Indoor Air Quality Strategies (page 119) promotes occupants comfort, wellbeing and productivity by improving indoor air quality with several options including ventilation. This optional credit has minor changes from LEED v4. LEED v4.1 BD+C Environmental Quality credit: Thermal Comfort (page 130) requires meeting requirements for both thermal comfort design and thermal comfort control. This optional credit has minor changes from LEED v4. This credit also has a pilot alternative compliance path available, Learning Controls for Thermal Comfort (view at https://www.usgbc.org/credits/new-construction-schools-new-construction-retail-new-construction-healthcare-data-centers-2 ) LEED v4.1 BD+C Environmental Quality credit: Indoor Air Quality Assessment (page 127) addresses ventilation as one of the pathways to ensure quality air in newly occupied buildings. Note: ventilation is also addressed in LEED v4.1 BD+C prerequisite: Environmental Tobacco Smoke Control (page 115) which has provisions to protect ventilation and air distribution systems from exposure to smoking outside the building. Finally, USGBC created a suite of pilot credits to support occupant wellness and health in light of particular risks and concerns posed by the COVID-19 pandemic. These pilot credits, which bear the label Safety First, are found here [https://www.usgbc.org/about/building-re-entry-resources] as well as in the pilot credit library. One of the Safety First pilot credits is available to LEED v4.1 BD+C projects and address ventilation -- Safety First: Design for Indoor Air Quality and Infection Control [https://www.usgbc.org/credits/safety-first-155-v4.1] Additional Safety First pilot credits could be used to inform building facilities operations and maintenance plans including ventilation, for example, Safety First: Managing Indoor Air Quality during COVID-19 [https://www.usgbc.org/credits/safety-first-138-v4.1] and Safety First: Maintenance of HVAC systems during COVID-19 [https://www.usgbc.org/credits/safety-first-156-v4.1]. These are optional credits. Another pilot credit that addresses ventilation is the pilot credit: Performance-based indoor air quality design and assessment which incorporates requirements of ASHRAE standard 62.1-2010. [View at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-18 ] | Mandatory/Optional | Yes | Yes | GP NC&M 4.1 Ventilation and Thermal Comfort | Fully | Green |  |  | Prerequisite: Environmental Quality - Minimum Indoor Air Quality Performance Credit: Environmental Quality - Thermal Comfort
Daylighting and lighting controls | GP NC&M 4.2 Daylighting and Lighting Controls | Page 23 | Yes | Two LEED v4.1 BD+C credits directly address daylighting and lighting controls. Environmental Quality credit: Daylight (page 134) addresses daylighting directly. This optional credit has minor changes from LEED v4. Environmental Quality credit: Interior Lighting (page 132) addresses lighting controls in supporting high quality interior lighting. This optional credit has no changes from LEED v4. Several pilot credits are available to projects that also address daylighting and lighting controls, such as Daylight in Nonregulalry Occupied Spaces [(view at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-42 ] | Optional | Yes | Yes | GP NC&M 4.2 Daylighting and Lighting Controls | Fully | Green |  |  | Credit: Environmental Quality - Daylight Credit: Environmental Quality - Interior Lighting
Low-emitting materials and products | GP NC&M 4.3 Low-Emitting Materials and Products | Page 23 | Yes | LEED v4.1 BD+C primarily addresses low – emitting materials through the Environmental Quality credit: Low-Emitting Materials (page 121).): Compliance with this credit includes requirements for VOC emissions into indoor air and the VOC content of materials. This optional credit had major changes from LEED v4. | Optional | Yes | Yes | GP NC&M 4.3 Low-Emitting Materials and Products | Fully | Green |  |  | Credit: Environmental Quality - Low-Emitting Materials
Radon mitigation | GP NC&M 4.4 Radon Mitigation | Page 24 | Yes | LEED v4.1 BD+C addresses radon mitigation in projects with residential units. If the project building contains residential units, each dwelling unit must meet the requirements of LEED v4.1 Multifamily EQ Prerequisite: Minimum Indoor Air Quality Performance, EQ Prerequisite Combustion venting and EQ Prerequisite Radon-resistant construction. This requirement is in the Environmental Quality prerequisite: Minimum Indoor Air Quality Performance (see page 114). | Mandatory | No | No | GP NC&M 4.4 Radon Mitigation | None | Red
Moisture and Mold control | GP NC&M 4.5 Moisture and Mold Control | Page 24 | Yes | Several LEED v4.1 BD+C credits address moisture control. Energy and Atmosphere credit: Enhanced Commissioning (page 73), addresses elements of moisture control through envelope commissioning which helps project teams catch and correct moisture control issues associated with the building envelope. Environmental Quality credit: Construction Indoor Air Quality Management Plan (page 125) requires meeting standards such as the protection of absorptive materials stored on-site and installed from moisture damage. Environmental Quality credit: Thermal Comfort (page 130) also addresses moisture including requirements for controllability of systems to enhance occupant comfort and well-being. Each of these optional credits had minor changes from LEED v4. | Optional | Yes | Yes | GP NC&M 4.5 Moisture and Mold Control | Partially | Yellow | To meet the Guiding Principles, agencies would need to ensure they develop and implement a moisture control plan or policy. The rating system has three credits that address moisture control; however, it does not require design teams to explicitly develop a plan for potential moisture control issues nor does it require implementation of any such plan. |  | Credit: Energy and Atmosphere - Enhanced Commissioning
Protecting IAQ during construction and operations | GP NC&M 4.6 Indoor Air Quality during Construction | Page 24 | Yes | LEED v4.1 BD+C addresses indoor air quality during construction primarily through the Environmental Quality credit: Construction Indoor Air Quality Management Plan (page 125). This is an optional credit that had minor changes from LEED v4. LEED v4.1 BD+C addresses indoor air quality during operations through a prerequisite and several credits. LEED v4.1 BD+C Environmental Quality prerequisite: Minimum Indoor Air Quality Performance (page 113) requires meeting standards and monitoring. This mandatory prerequisite has major changes from LEED v4. LEED v4.1 BD+C Environmental Quality credit: Enhanced Indoor Air Quality Strategies (page 119) promotes occupants comfort, wellbeing and productivity by improving indoor air quality. This optional credit has minor changes from LEED v4. LEED v4.1 BD+C Environmental Quality credit: Indoor Air Quality Assessment (page 127) addresses further strategies and monitoring to ensure quality air in newly occupied buildings. This optional credit has major changes from LEED v4. USGBC has created a suite of pilot credits to support occupant wellness and health in light of particular risks and concerns posed by the COVID-19 pandemic. These pilot credits, which bear the label Safety First, are found here [https://www.usgbc.org/about/building-re-entry-resources] as well as in the pilot credit library. One of the Safety First pilot credits is available to LEED v4.1 BD+C projects and address IAQ -- Safety First: Design for Indoor Air Quality and Infection Control [https://www.usgbc.org/credits/safety-first-155-v4.1] Additional Safety First pilot credits could be used to inform building facilities operations and maintenance plans including ventilation, for example, Safety First: Managing Indoor Air Quality during COVID-19 [https://www.usgbc.org/credits/safety-first-138-v4.1] and Safety First: Maintenance of HVAC systems during COVID-19 [https://www.usgbc.org/credits/safety-first-156-v4.1]. These are optional credits. Another pilot credit that addresses indoor air quality during operations is the pilot credit: Performance-based indoor air quality design and assessment which incorporates requirements of ASHRAE standard 62.1-2010. [View at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-18 ] | Mandatory/Optional | Yes | Yes | GP NC&M 4.6 Indoor Air Quality during Construction - Option 1 met - Environmental Quality credit: Construction Indoor Air Quality Management Plan requires the development and implementation of an indoor air quality (IAQ) management plan for the construction and preoccupancy phases of the building. | Fully | Green |  |  | Credit: Environmental Quality - Construction Indoor Air Quality Management Plan
Environmental smoking control | GP NC&M 4.7 Environmental Smoking Control | Page 24 | Yes | LEED v4.1 BD+C prerequisite: Environmental Tobacco Smoke Control (page 115) protects health by requiring prohibition of smoking inside as well as within defined areas where it could enter the building or impact people entering and exiting. This mandatory prerequisite had minor changes from LEED v4. | Mandatory | Yes | Yes | GP NC&M 4.7 Environmental Smoking Control - Option 1 met - LEED v4.1 BD+C prerequisite: Environmental Tobacco Smoke Control prohibits smoking outside the building except in designated smoking areas located at least 25 feet (7.5 meters) (or the maximum extent allowable by local codes) from all entries, outdoor air intakes, and operable windows. Communicate the no-smoking policy to occupants. Have in place provisions for enforcement or nosmoking signage. | Fully | Green |  |  | Prerequisite: Environmental Quality - Environmental Tobacco Smoke Control
Integrated pest management | GP NC&M 4.8 Integrated Pest Management | Page 25 | Yes | LEED v4.1 BD+C does not directly address pest management. However projects are encouraged to move directly into O+M after certification and there are two O+M credits addressing integrated pest management. | Optional | No | No | GP NC&M 4.8 Integrated Pest Management - LEED v4.1 BD+C does not directly address pest management. However projects are encouraged to move directly into O+M after certification and there are two O+M credits addressing integrated pest management. | None | Red
Occupant health and wellness | GP NC&M 4.9 Occupant Health and Wellness | Page 25 | Yes | Multiple prerequisites and credits in LEED v4.1 BD+C have a beneficial impact on occupant health and wellness. Those most directly connected with occupant health and wellness are all of those in the Indoor Environmental Quality (EQ) category: Prerequisite: Minimum Indoor Air Quality (page 113), Prerequisite: Environmental Tobacco Smoke (page 115); Prerequisite: Minimum Acoustic Performance (page 117); Credit: Enhanced Indoor Air Quality Strategies (page 119); Credit: Low-Emitting Materials (page 121); Credit: Construction Indoor Air Quality Management Plan (page 125); Credit: Indoor Air Quality Assessment (page 127); Credit: Thermal Comfort (page 130); Credit: Interior Lighting (page132); Credit: Daylight (page 134); Credit: Quality Views (page 138 ) and Credit: Acoustic Performance (page 140). The connection and intent for health and wellness is generally explained in the credit language. For additional context, see the Research Anthology of Health-Promoting Building Strategies. [view at https://www.usgbc.org/resources/research-anthology-health-promoting-building-strategies ] Other LEED v4.1 BD+C optional credits address occupant health and wellness through design and location that promote physical exercise and healthy, productive work spaces. Materials and Resources credits include points for inventories that may lead to improved human health outcomes. Location and Transportation credits for Surrounding Density and Diverse Use (page 16) and Bicycle Facilities (page 25) can facilitate daily physical activity. Sustainable Sites credits such as Open Space (page 38) provide options for reconnecting with nature and biophilia. The Safety First pilot credits also seek to address occupant health and wellness. [View https://www.usgbc.org/about/building-re-entry-resources ] One of the Safety First pilot credits is available to LEED v4.1 BD+C projects -- Safety First: Design for Indoor Air Quality and Infection Control [https://www.usgbc.org/credits/safety-first-155-v4.1] Additional Safety First pilot credits could be used to inform building facilities operations and maintenance plans for an occupant health outcome, for example, Safety First: Managing Indoor Air Quality during COVID-19 [https://www.usgbc.org/credits/safety-first-138-v4.1] and Safety First: Maintenance of HVAC systems during COVID-19 [https://www.usgbc.org/credits/safety-first-156-v4.1]. These are optional credits. Several additional pilot credits also support health and wellness. For example the pilot credit: Integrative Process for Health Promotion supports health outcomes through an early analysis to facilitate consideration of the project design on the health and well-being of its occupants and local community. | Optional | Yes | Yes | GP NC&M 4.9 Occupant Health and Wellness | Fully | Green |  |  | Credit: Location and Transportation - Surrounding Density and Diverse Use Credit: Location and Transportation - Bicycle Facilities Credit: Sustainable Sites - Open Space Credit: Indoor Environmental Quality - Daylight Credit: Indoor Environmental Quality - Views
Part II- Reduce the Environmental Impact of Materials
Materials with Recycled content | GP NC&M 5.1 Materials - Recycled Content | Page 26 | Yes | LEED v4.1 BD+C addresses recycled content with the Materials and Resources credit: Sourcing of Raw Materials (page 99). This credit has options for various environmentally preferable attributes, of which one is recycled content. This voluntary credit has major changes from LEED v4. | Optional | Yes | Yes | GP NC&M 5.1 Materials - Recycled Content | Partially | Yellow | To meet the Guiding Principles, agencies must purchase products that meet or exceed EPA's recycled content recommendations. The rating system combines several environmentally preferable attributes into a single credit for sourcing of raw material, including recycled content, but it cannot be assured that it will meet the Guiding Principles requirement.
Materials Biobased content | GP NC&M 5.2 Materials - Biobased Content | Page 26 | Yes | LEED v4.1 BD+C addresses biobased content with the Materials and Resources credit: Sourcing of Raw Materials (page 99). This credit has options for various environmentally preferable attributes, of which one is biobased content. This voluntary credit has major changes from LEED v4. | Optional | Yes | Yes | GP NC&M 5.2 Materials - Biobased Content | Fully | Green | While there are credits agencies can choose from to minimize harmful materials, there is no mention of the USDA Biopreferred program or products. In order to meet the guiding principles, agencies would need to ensure these products are used.
Environmentally preferable products | GP NC&M 5.3 Products | Page 26 | Yes | LEED v4.1 BD+C addresses environmentally preferable products through several credits. Materials and Resources credit: Sourcing of Raw Materials (page 99) has options for various environmentally preferable attributes. This voluntary credit has major changes from LEED v4. Materials and Resources credit: Environmental Product Declarations (page 97) also rewards projects for using products and materials with environmentally, economically, and socially preferable life-cycle impacts. This voluntary credit has major changes from LEED v4. Materials and Resources credit: Material Ingredients (page 101) also rewards projects for using products and materials verified to have improved life-cycle impacts. This voluntary credit has major changes from LEED v4. | Optional | Yes | Yes | GP NC&M 5.3 Products | Fully | Green |  |  | Credit: Materials and Resources - Environmental Product Declarations
Ozone depleting substances | GP NC&M 5.4 Ozone Depleting Substances | Page 26 | Yes | LEED v4.1 BD+C addresses ozone depleting substances directly through a prerequisite and a credit. Environment and Atmosphere prerequisite: Fundamental Refrigerant Management (page 72) requires avoiding the use of CRC-based refrigerants, or meeting specific conditions for reducing leakage and phase out. This is a mandatory prerequisite and had no changes from LEED v4. Environment and Atmosphere credit: Enhanced Refrigerant Management (page 88) rewards projects which have no refrigerants or low-impact refrigerants; or that comply with a maximum impact formula. This optional credit had no changes from LEED v4. In addition, two Materials and Resources optional credits incorporate criteria related to ozone. Materials and Resources credit: Building Life-Cycle Impact Reduction (page 94) rewards reduced environmental impacts over the building life cycle; one of the criteria which may be used is reducing depletion of the ozone layer (page 96). Materials and Resources credit: Environmental Product Declarations (page 97) recognizes products with verified improved environmental life-cycle impacts such as reducing depletion of the ozone layer. | Mandatory/Optional | Yes | Yes | GP NC&M 5.4 Ozone Depleting Substances | Fully | Green |  |  | Prerequisite: Environment and Atmosphere - Fundamental Refrigerant Management Credit: Environment and Atmosphere - Enhanced Refrigerant Management
Hazardous waste | GP NC&M 5.5 Hazardous Waste | Page 27 | Yes | LEED v4.1 BD+C supports proper management of hazardous waste during construction through excluding it from certain calculations in the Materials and Resources: Construction and Demolition Waste Management (page 111). In addition the system helps reduce the creation of hazardous waste through attention to materials and products with environmentally preferable characteristics. | None | No | No | GP NC&M 5.5 Hazardous Waste - Not Met - Although Materials and Resources: Construction and Demolition Waste Management supports proper management of hazardous waste during construction through excluding it from certain calculations, it does not necessarily comply with all relevant hazardous waste construction or operational activities that are covered by RCRA subtitle C and subtitle I and CERCLA. | N/A | Red
Solid waste management | GP NC&M 5.6 Solid Waste Management | Page 27 | Yes | Several LEED v4.1 BD+C credits address solid waste management. First, Materials and Resources prerequisite: Storage and Collection of Recyclables (page 91) is a mandatory prerequisite for LEED certification, requires dedicated areas for and the collection of recyclables during operations. This prerequisite had no changes from LEED v4. Several LEED v4.1 BD+C credits addresses construction waste management. Materials and Resources credit: Construction and Demolition Waste Management (page 111) requires projects to reuse, recover, and recycle nonhazardous construction and demolition materials. This optional credit has major changes from LEED v4. Materials and Resources credit: Building Life-Cycle Impact Reduction (page 94) requires project teams to reduce environmental effects by reusing existing building resources which inherently reduces waste. This optional credit has major changes from LEED v4. Pilot credits can also support solid waste management such as the pilot credit: Verified Construction & Demolition Recycling Rates | Mnadatory/Optional | Yes | Yes | GP NC&M 5.6 Solid Waste Management - Option 1 met - Materials and Resources credit: Construction and Demolition Waste Management requires projects to develop and implement a construction and demolition waste management plan and follow such plan to divert at least 50% of the total construction and demolition materials from landfills and incineration facilities. Additionally, it addresses preventing waste through reuse and source reduction design strategies. Salvage or recycle renovation and demolition debris and utilize waste minimizing design strategies for new construction elements. Track all materials generated by the project from start of construction through project completion to determine the project’s total waste generation (Although this is optional). | Fully | Green |  |  | Prerequisite: Materials and Resources - Storage and Collection of Recyclables Credit: Materials and Resources - Construction and Demolition Waste Management
Part II- Assess and Consider Building Resilience
Risk Assessment | GP NC&M 6.1 Risk Assessment | Page 28 | Yes | LEED v4.1 BD+C projects can address assessment of building risks such as from natural disasters or extreme weather through several credits and pilot credits. The Location and Transportation credit: Sensitive Land Protection (page 13) includes identifying sensitive land such as floodplains. This is an optional credit with minor changes from LEED v4. The Sustainable Sites credit: Site Assessment (page 34) also involves assessing site conditions to inform site design, and could help understand site risks and opportunities to improve resilience. Also, resilient design pilot credits, adapted from the RELi rating system, guide a team through risk assessment and resiliency improvements. See https://www.usgbc.org/resources/leed-resilient-design-pilot-credits-brief and links below under resilience. In addition, USGBC offers extensive resources for project teams to utilize to develop risk assessments and understand the potential impact of future conditions. See https://www.usgbc.org/resources/usgbc-case-studies-resilience and https://www.usgbc.org/about/programs/center-for-resilience Notably, LEED projects have access to the Arc platform, which offers embedded risk assessment tools, including a fee-based physical risk report from RiskFootprint. See https://arcskoru.com/new-tools-allow-arc-projects-understand-physical-risks | Optional | Yes | Yes | GP NC&M 6.1 Risk Assessment | Fully | Green |  |  | Credit: Location and Transportation - Sensitive Land Protection Credit: Sustainable Sites - Site Assessment
Building Resilience | GP NC&M 6.2 Building Resilience and Adaptation | Page 29 | Yes | LEED v4.1 BD+C addresses building resilience and adaptation in several ways. First, by requiring and incentivizing greater energy and water efficiency, buildings will be inherently more resilient such as by needing less external energy and water to function. Relevant mandatory prerequisites are Energy and Atmosphere prerequisite: Minimum Energy Performance (page 69) and Water Efficiency prerequisite: Indoor Water Use Reduction (page 53) as well as other EA and WE credits. Second, the LEED v4.1 BD+C EA Credit: Grid Harmonization (page 84) specifically addresses resilience and adaptation with approaches whereby the building works with the grid through demand response, load flexibility and management, and/or grid resilience strategies such as islanding. These approaches help the building reduce its contribution to grid stress as well as potentially support resilience, depending on the options used. Third, the encouragement of alternative water may lead to more resilient sources of water being available for sanitation and/or consumption in a power outage or emergency. The Safety First pilot credits related to designing the building for operations in light of COVID-19 can also contribute to resilience. See descriptions and links under “occupant health and wellness”. Additionally, LEED has several resilient design pilot credits to guide resiliency improvements. See https://www.usgbc.org/resources/leed-resilient-design-pilot-credits-brief These include Assessment and Planning for Resilience [view at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-26 ] and Design for Enhanced Resilience [view at https://www.usgbc.org/credits/new-construction-core-and-shell-schools-new-construction-retail-new-construction-27 ] USGBC offers extensive resources for project teams to utilize to develop risk assessments and understand the potential impact of future conditions. See https://www.usgbc.org/resources/profiles-resilience-leed-practice https://www.usgbc.org/resources/usgbc-case-studies-resilience and https://www.usgbc.org/about/programs/center-for-resilience | Mandatory | Yes | Yes | GP NC&M 6.2 Building Resilience and Adaptation | Fully | Green |  |  | Credit: Energy and Atmosphere - Grid Harmonization Credit: Water Efficiency - Alternative Water Pilot Credit: Assessment and Planning for Resilience Pilot Credit: Design for Enhanced Resilience

## Drop-Down (hidden)
3 options | 4 options
[SELECT]
[SELECT] | Yes
Yes | No
No | Partially Met
Issue with Response | Issue with Response