## Guidance
Guidance for Using the SFTool Guiding Principles Checklist
Overview:
This interactive version of the Guiding Principles for Sustainable Federal Buildings Criteria Checklist is a tool that can be used to demonstrate that a new construction or modernization project meets the intent of the Guiding Principles. Criteria on the checklist include both design elements and operational procedures that can be used to demonstrate continued operation as a sustainable Federal building after construction.
Criteria:
Core Criteria: Eighteen core criteria, supported by statutory and regulatory requirements and green building industry standards, are considered fundamental principles for any Federal high-performance green building (42 U.S.C. § 17061(13): https://uscode.house.gov/view.xhtml?req=17061&f=treesort&fq=true&num=5&hl=true&edition=prelim&granuleId=USC-prelim-title42-section17061). To qualify as a sustainable Federal building under the Guiding Principles the building must meet all 18 of the core criteria.
Non-Core Criteria: For the remaining 12 criteria that are not indicated as core, agencies must meet a minimum of 75 percent (9 of 12). Agencies have flexibility to focus on the criteria that are most applicable to the building and account for life cycle cost effectiveness, mission requirements, and unique project scopes.
If an agency determines that the building’s inherent function, mission, safety, or designation precludes it from meeting the minimum threshold of requisite criteria in a life cycle cost-effective manner as outlined above, the building would not qualify as a sustainable Federal building under this Guiding Principles. For the purposes of supporting the policy outlined in the Guiding Principles, those buildings that have met as many of the requisite criteria that are life cycle cost-effective may be designated as a Federal high-performance building (42 U.S.C § 17061(12): https://uscode.house.gov/view.xhtml?req=17061&f=treesort&fq=true&num=5&hl=true&edition=prelim&granuleId=USC-prelim-title42-section17061).
Agencies should continue to ensure all Federal statutes applicable to the project or building are met, regardless of whether the building is able to achieve the minimum criteria to be qualified as a sustainable Federal building.
Using the Checklist:
Criteria are indicated as 'CORE' or 'NON-CORE' and users can indicate in the drop-down cells in column F what criteria the project complies with. Compliant criteria will total at the top of column F. Percentage of compliant criteria will total at the top of column G.
Column G can be used to indicate what criteria, including which options, the project meets.
Column H can be used to indicate what evidence is required to demonstrate compliance.
SFTool Resources:
Links to SFTool tools and resources relevant to each criterion have been added after the criterion desciription and options.
Questions and Feedback: Please contact sftool@gsa.gov.

## Checklist
REFERENCE KEY
S | Criteria that are based on and reference statutory or regulatory requirements are indicated with “S” on the checklist. “S*” indicates NDAA-aligned criteria that are applicable to the U.S. Department of Defense (DoD).
Std | Criteria that are based on green building industry standards, rather than statutory or regulatory requirements, are indicated with “Std” on the checklist.
[C/I] | Criteria where campus-wide or installation-wide protocols, policies, contracts can be used to demonstrate, upon assessment, that the criteria were met at the building level are indicated on the checklist with a [C/I].
[5 empty] | Compliant Criteria (#) | Compliant Criteria (%)
|  | Total CORE Criteria (Target 100%) |  |  | 0 | 0%
|  | Total NON-CORE Criteria (Target 75%) |  |  | 0 | 0%
[5 empty] | CORE Compliant / NON-CORE Compliant | Meets Criterion / Option | Required Evidence of Compliance | Notes/Comments
1.0 - Employ Integrated Design Principles | 1.0 - Employ Integrated Design Principles
| NC&M Criteria 1.1 | Integrated Design and Management | CORE |  | Select…
(Std)
| Establish sustainability goals as part of the project to meet the Guiding Principles and incorporate those goals into the design document and process, such as the Owner’s Project Requirements (OPR), Basis of Design (BOD), Conceptual Design Report (CDR), or relevant design documents. | [5 empty] | Example: OPR, BOD, CDR, and relavant design documents indicating project sustainability goals.
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Use a collaborative, integrated process and team tailored to the size and function of the building to plan, program, design, construct, commission, and transition to operation the building project or modernization. Identify team members and roles. Ensure energy, water, materials, indoor environmental quality, recycling and composting, occupant health and wellness, transportation (including public transit, safety, parking, and electric vehicle charging), siting and landscape, the protection of historic properties and other cultural resources, community integration, and building resilience are considered while balancing the building’s function and mission throughout the design and construction of the building and into operations plans, where feasible. |  |  |  |  | Example: LEED Integrative Process Worksheet for the Integrative Process credits in the LEED BD+C and ID+C rating systems.
| Option 2 | Use an integrated design process consistent with 2018 International Green Construction Code (IgCC) Appendix F Integrated Design, including F101.1.1 (F1.1.1) Charrette Process (excluding F101.1.2 (F1.1.2) Design Charrette Matrix). |  |  |  |  | Example: Documentation of Integrated Design Process implemented consitent with 2018 IgCC Appendix F Charette Process (e.g., meeting minutes, summary report, etc.).
SFTool Resources
Use systems thinking to consider the effects and outcomes of planning and design processes and decisions.
Utilize an integrative process to set project goals and engage all stakeholders.
See real-world examples from five GSA project teams in how they used collaborative strategies to deliver high-performance buildings on time and on budget.
Follow sustainable strategies for planning and getting started in space reconfiguration, renovation, and construction projects.
| NC&M Criteria 1.2 | Sustainable Siting | CORE |  | Select…
|  |  | (S) | [C/I]
Follow all relevant requirements of 41 CFR § 102-76.20 of the Federal Management Regulation to make a positive contribution to the surrounding landscape,
and comply with the National Environmental Policy Act of 1969, as amended, 42 U.S.C. 4321 et seq.,
and the National Historic Preservation Act of 1966, as amended, 54 U.S.C. Subtitle III, Division A.
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | In alignment with sustainable siting best practices, assess all relevant opportunities for enhancements to the site sustainability and engage building occupants and other stakeholders utilizing the site. The specific actions of the site selection and planning stage should reflect the complexity of the proposed building and include, as appropriate, the following: 1) avoid development of prime farmland; 2) preserve areas with permeable soils; 3) avoid or, if not possible, minimize potential harm to or within the floodplain; 4) protect and conserve existing landscapes, wetlands, forest, and wilderness areas; 5) minimize site disturbance; 6) preserve threatened or endangered species and their habitats, including pollinators’ habitats; 7) improve linkages and connections to surrounding destinations and neighborhoods; 8) use historic properties, especially those located in central business districts; and 9) incorporate appropriate security design parameters. Incorporate these environmental considerations through a systematic interdisciplinary approach, and balance these concerns with cost and security. Agencies can reference additional siting resources, including GSA’S Sustainable Facilities Tool (SFTool) and
the Environmental Protection Agency (EPA’s) Smart Growth—Location and Green Building site,
the U.S. Department of Agriculture’s (USDA) pollinators resources, and
for projects involving historic properties, the Secretary of the Interior’s Standards for Rehabilitation & Illustrated Guidelines on Sustainability for Rehabilitating Historic Buildings.
| Option 2 | Conform to 2018 IgCC Section 501.3.1 (5.3.1) Site Selection and 501.3.2 (5.3.2) Predesign Site Inventory and Assessment.
SFTool Resources
Learn about environmentally responsible site selection.
| NC&M Criteria 1.3 | Stormwater Management | CORE |  | Select…
|  |  | (S) | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | For new construction or modernization projects disturbing a surface area of 5,000 or more square feet, use planning, design, construction, and maintenance strategies to maintain or restore the predevelopment hydrology of the property in terms of temperature, rate, volume, and duration of flow, in accordance with statutory requirements (42 U.S.C. § 17094). Low impact development (LID) infrastructure solutions can be utilized to help achieve this criteria.
| Option 2 | For new construction or modernization projects disturbing a surface area fewer than 5,000 square feet, use site planning, design, construction, and maintenance strategies such as low impact development (LID) to manage on-site stormwater and to maintain or restore hydrologic conditions after development, to the maximum extent that is technically practicable.
| Option 3 | Conform to 2018 IgCC Section 501.3.4 (5.3.4) Stormwater Management.
SFTool Resources
Explore water systems and their relationships to other building systems.
Learn about stormwater management.
Learn about how to minimize building water use.
| NC&M Criteria 1.4 | Infrastructure Utilization and Optimization | NON-CORE |  | Select…
|  |  | (Std) | [C/I]
Evaluate and prioritize transportation strategies and associated infrastructure improvements that promote and support alternative transportation, including walking, cycling, alternative fuel and electric vehicles, and public transit over the life of the building, as feasible and consistent with the mission of the facility.
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Locate any functional entry of the project within a ¼-mile (400-meter) walking distance of existing or planned bus, streetcar, shuttle, or informal transit stops, or within a ½-mile (800-meter) walking distance of existing or planned bus rapid transit stops, light or heavy rail stations, commuter rail stations or ferry terminals, except for those facilities where their mission and function prevents mass transportation access.
| Option 2 | Install electric vehicle charging stations for a minimum of two percent of the parking spaces created as part of the project or designated for the building occupants, where on-site vehicle parking is provided.
| Option 3 | Designate at least five percent of the parking spaces created as part of the project or designated for the building occupants as preferred parking for alternative fuel vehicles (may include parking for agency fleet alternative fuel vehicles).
| Option 4 | Provide an alternative transportation program to reduce congestion and the need for parking. The program may include transit services; walkability improvements including connections to transit, sidewalks, pathways, and bicycle trails; alternative transit education; designated rideshare areas; transit subsidies; telecommuting incentives; or bicycle racks and showers. and showers.
| Option 5 | Prior to and during the space decision process, engage planning officials at the state, metropolitan, or municipal level to identify ways proposed agency actions can support community sustainability and potentially align with local and regional long range plans and objectives. Support and integrate proposed actions into the project.
| Option 6 | Conform to 2018 IGCC Section 1001.3.2.4 (10.3.2.4) Transportation Management Plan and
Section 501.3.7.3 (5.3.7.3) Site Vehicle Provisions.
SFTool Resources
Learn about environmentally responsible site selection.
Learn about electric vehicles and electric vehicle supply equipment.
| NC&M Criteria 1.5 | Commissioning | CORE |  | Select…
(S)
Employ commissioning, as defined per Section 432 of the Energy Independence and Security Act of 2007 (42 U.S.C. 8253(f)(1)(A)), and tailored to the size and complexity of the building.
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Document through a commissioning process that the building and its commissioned components, assemblies, and systems (including any renewable energy systems, thermal storage, district heating and cooling system, and cooling towers) comply with the owner’s project requirements. Conduct commissioning in accordance with the U.S. Department of Energy (DOE) Federal Energy Management Program's (FEMP) Commissioning for Federal Facilities guidance, using ANSI/ASHRAE/IES Standard 202 or other generally accepted engineering standards, guidelines, and nationally recognized organizations. For less complex buildings, commissioning should be performed with generally accepted engineering standards acceptable to the agency. A certified commissioning provider (may include a qualified agency employee), independent of the design and construction or operating team, should provide, within one year of project completion, a final commissioning report.
| Option 2 | Conform to 2018 IgCC Section 1001.3.1.2 (10.3.1.2) Building Project Commissioning (Cx) Process.
SFTool Resources
Explore the system impacts of commissioning the HVAC system to achieve sustained performance over time.
Follow sustainable strategies for structure/envelope in space reconfiguration, renovation, and construction projects.
2.0 Optimize Energy Performance | 2.0 Optimize Energy Performance
| NC&M Criteria 2.1 | Energy Efficiency | CORE |  | Select…
(S)
For New Construction:
Ensure compliance with Federal energy efficiency performance requirements for new construction in accordance with § 109 of the Energy Policy Act of 2005 (42 U.S.C. § 6834(a)(3)(A)) and DOE’s regulations as established under
10 CFR parts 433, subpart A, and
10 CFR parts 435, subpart A.
Ensure installation of ENERGY STAR and
FEMP-designated products in all procurements involving energy-consuming products and services, in accordance with
42 U.S.C § 8259b and
10 CFR § 436.40–436.43.
For Modernization projects:
Ensure installation of ENERGY STAR and
FEMP-designated products in all procurements involving energy-consuming products and services, in accordance with
42 U.S.C § 8259b and
10 CFR § 436.40–436.43.
Employ strategies to improve energy performance and reduce energy usage in accordance with 42 U.S.C. § 8253(a).
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Ensure building energy use is 20 percent below a FY 2015 energy use baseline.
| Option 2 | Ensure building energy use is 30 percent below a FY 2003 energy use baseline.
| Option 3 | Ensure the building has an ENERGY STAR score of 75 or higher.
| Option 4 | For building types not eligible to receive an ENERGY STAR score and where adequate benchmarking data exists, demonstrate that the building is in the top quartile of energy performance for its building type.
| Option 5 | Follow the Federal energy performance requirements established under 10 CFR Parts 433 and 435 by designing to exceed ANSI/ASHRAE/IES Standard 90.1 by at least 30 percent, where life cycle cost-effective.
SFTool Resources
Learn about building decarbonization.
Learn about how to minimize building energy use and emissions.
Follow sustainable strategies for structure/envelope in space reconfiguration, renovation, and construction projects to optimize energy performance.
Follow sustainable strategies for electrical systems to improve energy use.
Follow sustainable strategies for mechanical systems to improve energy use.
Identify potential cost-effective facility upgrades.
Discover bundling strategies to realize cost savings.
| NC&M Criteria 2.2 | Energy Metering | CORE |  | Select…
(S)
Install building-level meters for electricity and advanced meters to the maximum extent practicable, as required by EPAct 2005 § 103 (42 U.S.C. § 8253(e)). Install standard or advanced meters for natural gas and steam to the maximum extent practical, in accordance
with the DOE’s Federal Building Metering Guidance and
EISA 2007 § 434 (42 U.S.C. § 8253(e)(1)).
SFTool Resources
Explore submetering systems and their relationships to other building systems.
Use the Submetering Wizard to learn about submetering techniques and benefits by system.
| NC&M Criteria 2.3 | Renewable Energy | NON-CORE |  | Select…
|  |  | (S) | [C/I]
Evaluate applicable renewable electric energy strategies related to the project or building that could support, as needed, agency progress toward renewable energy goals where cost-effective, per 42 U.S.C. § 15852(a). [Campus/Installation-wide approach can be utilized if the agency has assessed and can verify that the building will directly benefit from the renewable energy system. Alternatively, the agency should develop an internal energy accounting or tracking system to apportion renewable energy or attributes to the building to avoid any double counting.]
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Implement, as appropriate, life cycle cost-effective on-site renewable electric or thermal energy projects. Alternatively, utilize alternative energy systems such as waste heat, combined heat and power (CHP), or fuel cell energy systems, where life cycle cost-effective. If on-site renewable energy or alternative energy systems are not technically feasible or life cycle cost-effective, the agency should establish an internal energy accounting or tracking system to apportion power purchases from off-site renewable sources or renewable energy certificates (RECs) to the building, as aligned with agency plans.
| Option 2 | Where appropriate and life cycle cost-effective, not less than 30 percent of the hot water demand is to be met through the installation and use of solar hot water heaters, per 42 U.S.C § 6834(a)(3)(A)(iii).
| Option 3 | Conform to 2018 IgCC Section 701.4.1.1 (7.4.1.1) On-Site Renewable Energy Systems or equivalent, with the exception that there is no minimum energy production (kBtu/ft2) requirement.
SFTool Resources
Learn about building decarbonization.
Learn about renewable energy.
Learn about solar/photovoltaic systems.
| NC&M Criteria 2.4 | Benchmarking | CORE |  | Select…
(S)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Benchmark building performance at least annually, preferably using ENERGY STAR Portfolio Manager, and regularly monitor building energy performance against historic performance data and peer buildings, in
accordance with criteria established by DOE’s Federal Building Energy Use Benchmarking Guidance per
42 U.S.C. § 8253(f)(8).
| Option 2 | Conform to 2018 IgCC Section 1001.3.2.1.3.2 (10.3.2.1.3.2) Track and Assess Energy Consumption.
SFTool Resources
3.0 - Protect and Conserve Water | 3.0 - Protect and Conserve Water
| NC&M Criteria 3.1 | Indoor Water Use | CORE |  | Select…
(S)
For new construction where water is used to achieve energy efficiency, water conservation measures must be applied to the extent that they are life cycle cost-effective in accordance with 10 CFR Parts 433 and 435. In addition to the use of water conservation technologies otherwise required by 42 U.S.C. § 6834, water conservation technologies are to be applied to the extent that the technologies are life cycle cost-effective for new construction and modernization projects, in accordance with 42 U.S.C. § 6834(a)(3)(D)(vii).
Eliminate the use of single-pass (also called "once-through") cooling equipment using potable water and optimize cooling tower operations to minimize makeup water. Agencies should refer to EPA's WaterSense,
GSA’s SFTool: Water, and
DOE-FEMP’s Water Efficiency in Federal Buildings and Campuses resources for additional details on available water conservation technologies and best management practices.
For New Construction:
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Install WaterSense equipment or equivalent alternatives, where available, for all fixtures that are designed to be used more than once per day on average over a month. For all fixtures and fittings using potable water with planned use of more than once per day, compile cut sheet or product declarations or plumbing schedule showing flush or flow rate performance meeting WaterSense or equivalent.
| Option 2 | Conform to 2018 IgCC Section 601.3.2.1 (6.3.2.1) Plumbing Fixtures and Fittings or 601.3.2.6 (6.3.2.6) Medical and Laboratory Facilities (if applicable).
For Modernization projects:
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Install WaterSense equipment or equivalent alternatives to demonstrate at least a 20 percent reduction when comparing installed fixture performance to a base case representing the code-minimum, using the FEMP Water Evaluation Data Tool or other water fixture performance calculator. For all fixtures and fittings using potable water with planned use of more than once a day, compile cut sheet or product declarations or plumbing schedule showing flush or flow rate performance consistent with WaterSense or equivalent.
| Option 2 | Conform to 2018 IgCC Section 601.3.2.1 (6.3.2.1) Plumbing Fixtures and Fittings or 601.3.2.6 (6.3.2.6) Medical and Laboratory Facilities (if applicable).
SFTool Resources
Explore water systems and their relationships to other building systems.
Learn about how to minimize building water use.
Follow sustainable strategies for plumbing systems to improve water use.
| NC&M Criteria 3.2 | Water Metering | CORE |  | Select…
(Std)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Install building level water meters (standard or advanced) and monitor to ensure optimized management of water use during occupancy, including detection of leaks in accordance with DOE’s Federal Building Metering Guidance.
| Option 2 | Conform to 2018 IgCC Section 601.3.4.1 (6.3.4.1) Consumption Management.
SFTool Resources
Explore submetering systems and their relationships to other building systems.
Use the Submetering Wizard to learn about submetering techniques and benefits by system.
| NC&M Criteria 3.3 | Outdoor Water Use | NON-CORE |  | Select…
|  |  | (Std) | [C/I]
Evaluate and implement, as applicable, water efficient landscaping best practices that incorporate native, non-invasive, drought tolerant, and low maintenance plant species. Utilize and follow, as appropriate, landscaping best practices provided by GSA’s SFTool - Water resources,
DOE-FEMP’s Water Efficiency in Federal Buildings and Campuses resources,
EPA’s WaterSense - Outdoors resources, or an agency-approved tool.
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Employ water efficient irrigation strategies to reduce outdoor potable water consumption. Where installed, demonstrate that the permanent irrigation system uses 50 percent or less of the amount of potable water used in conventional practices, assuming typical annual baseline water use. Refer to DOE-FEMP’s Water Efficiency in Federal Buildings and Campuses resource on establishing a baseline. Install water meters for irrigation systems serving more than 25,000 square feet of landscaping.
| Option 2 | If installing landscaping, utilize xeriscaping techniques or do not irrigate beyond the establishment of plantings.
| Option 3 | Conform to 2018 IgCC Section 601.3.1.1 (6.3.1.1) Landscape Design. If irrigation is used, conform to Section 601.3.1.2 (6.3.1.2) Irrigation and Section 601.3.4.1 (6.3.4.1) Consumption Management (for irrigated landscaped areas greater than 25,000 square feet).
SFTool Resources
Explore water systems and their relationships to other building systems.
Learn about how to minimize building water use.
| NC&M Criteria 3.4 | Alternative Water | NON-CORE |  | Select…
|  |  | (Std) | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Implement life-cycle cost-effective methods to utilize alternative sources of water for indoor or outdoor use, such as harvested rainwater, treated wastewater, air handler condensate capture, grey water, and reclaimed water, where permitted by local laws and regulations.
| Option 2 | Implement life-cycle cost-effective methods to utilize alternative sources of water that conform to the 2018 IgCC Definition of Water, Alternative on-site sources.
SFTool Resources
Explore water systems and their relationships to other building systems.
Learn about water reuse and recycling.
Learn about how to minimize building water use.
4.0 - Enhance the Indoor Environment | 4.0 - Enhance the Indoor Environment
| NC&M Criteria 4.1 | Ventilation and Thermal Comfort | CORE |  | Select…
(S)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | In accordance with 41 CFR §§ 102-74.195 and 102-74.185 of the Federal Management Regulation, comply
with all ventilation and thermal comfort requirements. Utilize the most current version of ASHRAE “Ventilation for Acceptable Indoor Air Quality” Standard 62.1 or 62.2 and ASHRAE 55 "Thermal Environmental Conditions for Human Occupancy" as specified by the Federal Management Regulation. Agencies should refer to the GSA’s SFTool Enhancing Health with Indoor Air resources on enhancing indoor air quality.
| Option 2 | Conform to 2018 IgCC Sections 801.3.1 (8.3.1) Indoor Air Quality and 801.3.2 (8.3.2) Thermal Environmental Conditions for Human Occupancy.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
Learn about enhancing health with indoor air.
| NC&M Criteria 4.2 | Daylighting and Lighting Controls | NON-CORE |  | Select…
(S)
Design and construct the building to meet and maintain all required illumination levels, in accordance with 41 CFR § 102-74.180 of the Federal Management Regulation, and maximize the use of automatic dimming controls or accessible manual controls in regularly occupied spaces.
AND ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Improve access to and benefits from daylight by ensuring regularly occupied spaces along the exterior wall have fenestration, and control solar gain, daylight transmittance, and glare. If the building cannot achieve adequate daylighting due to mission or security needs, utilize circadian-effective lighting based on computer analysis or simulation tools to design optimal lighting conditions for the regularly occupied spaces. Evaluate and assess occupant workplace to allow more open space around windows, except where not appropriate because of building function, mission, or structural constraints.
| Option 2 | Conform to 2018 IgCC Sections 801.3.7 (8.3.7) Glare Control, 801.4.1.1.1 (8.4.1.1.1) Minimum Daylight Area, and 801.4.1.2 (8.4.1.2) Minimum Sidelighting Effective Aperture for Office Spaces and Classrooms, and 801.4.1.3 (8.4.1.3) Shading for Offices; or 801.5.1 (8.5.1) Daylight Simulation.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
Explore lighting systems and their relationships to other building systems.
Learn about daylighting.
Learn about lighting control.
Learn about circadian light.
| NC&M Criteria 4.3 | Low-Emitting Materials and Products | NON-CORE |  | Select…
|  |  | (Std) | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Utilize low-emitting (low or no volatile organic compound (VOC)) materials, on at least 75 percent of interior products by cost or surface area, for the following materials and products: composite wood products, flooring and carpet systems, wall panels, insulation, adhesives, sealants, interior paints and finishes, solvents, janitorial supplies, and furnishings. Agencies should refer to EPA’s Volatile Organic Compounds’ Impact on Indoor Air Quality resources for information on low-emitting products.
| Option 2 | Conform to 2018 IgCC Section 801.4.2 (8.4.2) Materials or Section 801.5.2 (8.5.2) Materials.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
Learn about low-emitting materials.
Follow sustainable strategies for materials and finishes selection in space reconfiguration, renovation, and construction projects to protect indoor environmental quality.
| NC&M Criteria 4.4 | Radon Mitigation | CORE |  | Select…
|  |  | (S) | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | In accordance with 41 CFR § 102-80.20 of the Federal Management Regulation, test for radon and mitigate high levels to maintain a level at or below 4 pCi/L (picocuries/liter).
| Option 2 | Conform to 2018 IgCC Section 1001.3.1.9 (10.3.1.9) Soil-Gas Control.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
| NC&M Criteria 4.5 | Moisture and Mold Control | NON-CORE |  | Select…
(Std)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Implement a moisture control strategy (may be part of the operations and maintenance protocols) for controlling moisture flows and condensation to prevent building damage, minimize mold contamination, and reduce health risks related to moisture.
| Option 2 | Conform to 2018 IgCC Section 801.3.6 (8.3.6) Moisture Control.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
| NC&M Criteria 4.6 | Indoor Air Quality during Construction | NON-CORE |  | Select…
(Std)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Develop and implement a plan to protect indoor air quality during construction.
| Option 2 | Conform to 2018 IgCC Sections 1001.3.1.5 (10.3.1.5) IAQ Construction Management, and 1001.3.1.8 (10.3.1.8) Construction Activity Pollution Prevention: Protection of Occupied Areas.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
Follow sustainable strategies for construction in space reconfiguration, renovation, and construction projects to protect indoor environmental quality.
| NC&M Criteria 4.7 | Environmental Smoking Control | CORE |  | Select…
|  |  | (S) | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | In accordance with 41 CFR § 102-74.315 and 102-74.330 of the Federal Management Regulation, prohibit smoking in any form inside and within 25 feet of all building entrances, operable windows, and building ventilation intakes. Ensure signage is installed as appropriate.
| Option 2 | Conform to 2018 IgCC Section 801.3.1.7 (8.3.1.7) Environmental Tobacco Smoke.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
| NC&M Criteria 4.8 | Integrated Pest Management | CORE |  | Select…
|  |  | (S) | [C/I]
In accordance with 41 CFR § 102-74.35 of the Federal Management Regulation, ensure effective and environmentally sensitive integrated pest management (IPM) services including the planning, development, operations, and maintenance for pest control, removal, and prevention in both indoor and outdoor spaces. Ensure that pest management contracts are effectively coordinated with the activities of other building service programs that have a bearing on pest activity, such as food service, landscaping, child care, waste management, and repairs and operations.
Refer to GSA’s IPM definition,
EPA’s IPM resources, and
GSA’s SFTool Pest Management resources for additional program guidance.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
Learn about procuring pest management services.
| NC&M Criteria 4.9 | Occupant Health and Wellness | CORE |  | Select…
(Std)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Evaluate the feasibility of implementing occupant health and wellness efforts and promote two or more strategies that are cost-effective and applicable to the building mission. Agencies are encouraged to assess and promote universally accepted workplace occupant health and wellness strategies most appropriate to their building and mission. Agencies should refer to GSA’s SFTool for additional strategies and guidance on health and wellness in Federal facilities.
Examples of common health and wellness strategies include, but are not limited to: 1) Implementing biophilic design strategies that connect a majority of interior spaces with nature, using views, finishes, plants, daylighting, outdoor access, or other strategies; 2) Providing healthy dining options in the building or on campus that support offering a variety of fresh food options for occupants, following the U.S Department of Health and Human Services (HHS) / GSA Health and Sustainability Guidelines for Federal Concessions and Vending Operations where appropriate;
3) Designing stairwells as a desirable option for circulation to support active occupants; 4) Implementing a fitness program, including constructing or providing access to a fitness center or multi-use space for exercise in the building, on-site, or on campus; 5) Installing bicycle parking with safe, secure storage; 6) Providing adjustable-height desks or computer risers for 25 percent of the regular occupied spaces; and 7) Providing water bottle-refilling stations, establish a process to test water quality annually, and ensure proper maintenance of the stations. Refer to EPA’s Drinking Water resources for additional guidelines.
| Option 2 | Achieve certification utilizing any Health & Wellness Standards and Rating System identified by GSA, under
its authorities per 42 U.S.C. § 17092.
SFTool Resources
Explore IEQ systems and their relationships to other building systems.
Learn how building design can impact the health of occupants.
Learn about biophilia and design.
Learn how to enhance human health, comfort, and performance by improving indoor air.
Learn how to promote productivity, health and wellbeing while working from home.
Follow sustainable strategies for occupant health and wellness in space reconfiguration, renovation, and construction projects to promote physical activity.
Follow sustainable strategies for occupant health and wellness in space reconfiguration, renovation, and construction projects to design for psychological wellbeing.
Follow sustainable strategies for occupant health and wellness in space reconfiguration, renovation, and construction projects to design workspaces to minimize stress and strain on the body.
Benchmark workplace quality and measure improvements.
Take a virtual your of a healthy workplace for design guidance, federal requirements and to compare materials for various workspaces.
5.0 - Reduce the Environmental Impact of Materials | 5.0 - Reduce the Environmental Impact of Materials
| NC&M Criteria 5.1 | Materials - Recycled Content | CORE |  | Select…
|  |  | (S) | [C/I]
Use Resource Conservation and Recovery Act (RCRA) section 6002 compliant products that meet or exceed EPA’s Comprehensive Procurement Guideline Program, which provides recycled content recommendations for building construction, modifications,
operations, and maintenance, in accordance with 42 U.S.C. § 6962 et seq.
SFTool Resources
Use Life Cycle Thinking as a decision-making tool when selecting products and materials.
Follow sustainable strategies for materials and finishes selection in space reconfiguration, renovation, and construction projects.
Compare materials and systems to understand their sustainable attributes.
Browse products within the Green Procurement Compilation.
Identify compliant brand-name products with SFTool Product Search.
View sample contract language for procuring products that meet environmental programs.
Verify contractor compliance with sustainability requirements for products and materials.
| NC&M Criteria 5.2 | Materials - Biobased Content | CORE |  | Select…
|  |  | (S) | [C/I]
Use U.S. Department of Agriculture (USDA) BioPreferred products, which are designated products with the highest content level per
USDA’s biobased content recommendations, in accordance with 7 U.S.C. § 8102.
SFTool Resources
Use Life Cycle Thinking as a decision-making tool when selecting products and materials.
Follow sustainable strategies for materials and finishes selection in space reconfiguration, renovation, and construction projects.
Compare materials and systems to understand their sustainable attributes.
Browse products within the Green Procurement Compilation.
Identify compliant brand-name products with SFTool Product Search.
View sample contract language for procuring products that meet environmental programs.
Verify contractor compliance with sustainability requirements for products and materials.
| NC&M Criteria 5.3 | Products | NON-CORE |  | Select…
(Std)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Use construction products and building supplies recommended under EPA’s Recommendations of Specifications, Standards, and Ecolabels for Federal Purchasing, as appropriate and applicable.
| Option 2 | Conform to 2018 IgCC Section 901.4.1.4 (9.4.1.4) Multiple-Attribute Product Declaration or Certification.
SFTool Resources
Use Life Cycle Thinking as a decision-making tool when selecting products and materials.
Follow sustainable strategies for materials and finishes selection in space reconfiguration, renovation, and construction projects.
Compare materials and systems to understand their sustainable attributes.
Browse products within the Green Procurement Compilation.
Identify compliant brand-name products with SFTool Product Search.
View sample contract language for procuring products that meet environmental programs.
Verify contractor compliance with sustainability requirements for products and materials.
| NC&M Criteria 5.4 | Ozone Depleting Substances | CORE |  | Select…
|  |  | (S) | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Ensure compliance with 42 U.S.C. § 7671k and
42 U.S.C. § 7671l, concerning the procurement of safe alternatives for ozone depleting substances.
Maximize the use of safe alternatives, where EPA’s Significant New Alternative Policy (SNAP) Program has identified acceptable substitutes and alternatives. Refer to EPA's SNAP regulations, 40 CFR part 82, which list substitutes that have been determined unacceptable, acceptable to use conditions, and acceptable subject to narrowed use limits.
| Option 2 | Conform to 2018 IgCC Section 901.3.3 (9.3.3) Refrigerants.
SFTool Resources
Learn about building decarbonization.
Learn about strategies to reduce the impact of refrigerants.
| NC&M Criteria 5.5 | Hazardous Waste | CORE |  | Select…
(S)
Ensure compliance with all relevant hazardous waste construction or operational activities that are covered by RCRA subtitle C and subtitle I and the Comprehensive Environmental Response, Compensation, and Liability Act (CERCLA), per 42 U.S.C. § 9601 et seq. and
its implementing regulations at 40 CFR Parts 239-282. This criterion is achieved so long as it can be demonstrated that the building has a program and procedure to manage hazardous waste, or the building does not generate, store, treat, or dispose of hazardous waste. (40 CFR §§ 260.10 and 261.3).
SFTool Resources
| NC&M Criteria 5.6 | Solid Waste Management | NON-CORE |  | Select…
(Std)
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Develop and implement a construction and demolition waste management plan. Where markets exist, divert at least 50 percent of construction and demolition materials from landfills and non-energy generating incinerations, as defined by and in alignment with EPA’s Waste Management Hierarchy. AND Design the building to incorporate appropriate space, equipment, and transport accommodations for collection, storage, and staging of recyclables and, as appropriate, compostable materials.
| Option 2 | Conform to 2018 IgCC Section 901.3.1.1 (9.3.1.1) Diversion. AND Conform to 2018 IgCC Section 901.3.4 (9.3.4) Areas for Storage and Collection of Recyclables and Discarded Goods.
SFTool Resources
Explore solid waste systems and their relationships to other building systems.
Learn about materials and resources.
6.0 - Assess and Consider Building Resilience | 6.0 - Assess and Consider Building Resilience
| NC&M Criteria 6.1 | Risk Assessment | NON-CORE |  | Select…
|  |  | S* | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Conduct a regionally tailored risk assessment for the site that, where appropriate, aims to: 1. Assess long-term mission critical functions over the intended service life by incorporating considerations such as mission needs, building functions, occupants, and operations. Consider impacts to the surrounding community and to building operational needs. 2. Assess the localized risks to the design life of the building, which involves identifying hazards, threats, vulnerabilities, and consequences. During the hazard identification step, identify and review any known observed and expected long-term weather-related and geographical hazards to inform and enhance the resilience of the building design and operations. 3. Assess relevant stressors that could exacerbate hazards and risks to the building and operations. Account for whether the frequency is increasing, remaining the same, or decreasing in the specific region. 4. Evaluate and consider the adaptive capacity of the building and operations to cope with shocks and stressors, or ability to adjust to new situations. 5. Incorporate, as applicable, a comprehensive energy and water infrastructure assessment to ensure resilience and investigate alternative energy sources to serve as back-up power.
| Option 2 | Ensure that the building, as well as any planned mission critical activities housed in the building, have been evaluated and integrated as part of a recent agency, facility, installation, or campus resilience or adaptation assessment. This can include any resilience and adaptation assessment activities associated with Installation Master Plans, climate adaptation plans, or equivalent agency, installation, or campus resilience or adaptation plans.
| Option 3 | Utilize available Federal climate resilience planning tools to inform the decision making and design for the building project. Available tools include the U.S. Climate Resilience Toolkit,
the Naval Facilities Engineering Command’s Climate Change Installation Adaptation and Resilience Planning Handbook,
the NIST Community Resilience Planning Guide for Buildings and Infrastructure Systems,
the NIST EDGe$ (Economic Decision Guide Software) Online Tool,
the U.S. Army Corps of Engineers climate preparedness and resilience planning tools,
the U.S. Department of the Army’s Climate Assessment Tool and
Climate Resilience Handbook,
FEMP’s Technical Resilience Navigator, or any other Federal agency-developed climate resilience or adaptation planning tools that become available.
SFTool Resources
Manage climate risk by developing resilience plans.
Explore climate terms and tools.
| NC&M Criteria 6.2 | Building Resilience and Adaptation | NON-CORE |  | Select…
|  |  | S* | [C/I]
CHOOSE ONE OF THE FOLLOWING OPTIONS:
| Option 1 | Utilize the risk assessment to determine and prioritize design parameters that should be incorporated to ensure resilient building design and operations over the intended service life of the building, considering mission criticality, cost, and security. Ensure the implementation of no cost and cost-effective climate resilience measures, and, where feasible, implement solutions that focus on operations. Consider in the operation plans of the building, facility, campus, or installation, the adaptive capacity of the building to cope with stressors and mitigate based on mission criticality and cost. Identify and implement measures, where appropriate, to support passive survivability and functionality during emergencies.
| Option 2 | Ensure the implementation of cost-effective strategies identified through an agency developed resilience or adaptation plans or any other Federal agency developed climate resilience or risk assessment planning tools. (For examples of available tools, refer to criteria 6.1.)
SFTool Resources
Manage climate risk by developing resilience plans.
Explore climate terms and tools.

## DataValidation (hidden)
Compliance
Select…
Yes
No
In-Progress
Not Applicable